## DH zone evaluation
|  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | input cells
Zone name (acronym) |  | industrial | sfh
Heat density | GWh/km²/a = kWh/m²/a = 10 MWh/ha/a | 45 | 25 |  |  |  | Heat demand (space heating, domestic warm water, process heat) in relation to the base area of the supply area (zone)
Connection rate | % | 75% | 60% |  |  |  | Expected ratio of connected to existing buildings in the zone
Linear heat density (estimated) | kWh/m/a | 2565 | 1140 |  |  |  | Estimated reference value for the achievable linear heat density (in relation to route length)
Alternative input of the annual heat demand and the route length
Annual heat demand | MWh/a | [5 empty] | Annual heat demand of (new) customers (sum of key/potential customers customers in the zone)
Route length | m | [5 empty] | Estimated route length ("trench length" in metres - total length of route for main, branch and house connections)
Linear heat density | kWh/m/a | [5 empty] | Linear heat density (annual heat demand / route length)
Feasibility assessment for district heating grid (expansion) - indicative!
Heat density | GWh/km²/a | 45 | 25
Linear heat density | kWh/m/a | 2565 | 1140 |  |  |  |  | Linear heat density >= kWh/m/a | Heat distribution losses (district heating network) | Legend for evaluation from an efficiency perspective | Economic feasibility with >= GWh/km²/a 1)
Evaluation from an efficiency perspective (heat distribution losses) |  | very good | limited |  |  |  | see also the table on the right for feasibility assessment data base | 1800 | Heat distribution losses ≤ 10 % (target value QM system) achievable with conventional piping technology and standard grid temperatures | very good
Evaluation of economic feasibility |  | good | limited |  |  |  |  | 1500 | Compliance with Austrian (subsidy) criterion of minimum 75 % overall efficiency (maximum approx. 12 % distribution losses) conventionally possible | good | 40
Both heat distribution losses and economic feasibility must be assessed in detail, taking into account local conditions (e.g. locally strongly differing excavation costs, prices, etc.)! As reference a DH network (expansion) is feasible from 22,5 GWh/km²/a heat density at 70 % connection rate (rated as "limited"; in urban supply area from about 40 - rated as "good"). 1) | [7 empty] | 800 | Low heat distribution losses only achieveable with higher insulation standard / double pipes / low network temperatures | limited | 22.5
[8 empty] | below 800 | Low heat distribution losses only achieveable with innovative technologies (e.g. low-temperature ditrict heating, innovative storage/load management) | critical
1) feasibility limits according to (experience) data for Austria