## README
This tool was developed as part of the Interreg Central Europe project CE200535 HEAT 35 Transforming district heating systems of Central Europe into sustainable and efficient heating and cooling systems by 2035
Please contact AEE INTEC for any suggestions or bug-reports about this tool:
Christian Ramerstorfer - c.ramerstorfer@aee.at
Version 17.03.2026

## Explanatory notes
Introduction
The purpose of this Excel tool is to provide an overview of estimated average annual heat production costs for various heat supply portfolios, based on a 20-year operational period. This enables district heating operators to compare their current system with alternative heat supply portfolios when planning refurbishments or future investments. In addition, the tool estimates the CO2-equivalent missiosn of each portfolio. The tool is not designed to deliver precise, project-specific cost calculations. Due to the complexity and site-specific characteristics of different heating technologies, such accuracy would require a more detailed engineering and economic analyses. Instead, the tool applies a simplified approach to provide a fast and transparent comparison using indicative values. Because of this, all results should be interpreted with care. Users should always consider local conditions, the assumptions applied to the input data, and the simplified methodology on which the tool is based.
Main notes
This Excel tool is organized into the following worksheets: - Exploratory notes - Boundary conditions (fuel prices and CO2 emission factors) - RES Alternatives (main inputs and results) - HelpSheet (supporting calculations - not to be changed)
Boundary conditions
In the boundary conditions sheet, users define the global (i.e., case-independent) technical, economic and ecological parameters used in the calculations. Default values are given for Austria. Please ensure that the values you enter are representative, consistent, and based on an uniform, up-tp-date, and meaningful year. For each main fuel type, the following parameters can be specified:
Net heating value (NCV): The net heating value (or net calorific value NCV) is the amount of heat released during complete combustion without considering the condensation heat of water (as it is usually dissipated as unused steam). Beware that, though it is possible to change the net heating value, it might be only necessary to revise this value for biomass fuels where depending on the exact source (e.g. wood type, water content, ...) relevant differences on the net heating value can be observed. Fuel price: fuel prices should be referred to a specific and representative year (the same or similar for all fuels). Average price development: This is the expected annual percentage change in fuel prices over the next 20 years. The tool assumes a constant percentage increase each year. Given the uncertainty and strong influence of fuel price trends on the results, it is advisable to apply conservative assumptions. Average heat price 20-years: Based on the reference-year fuel price and the assumed average price development, the tool calculates an average heat price for the 20-year period. This value is later used in the evaluation of the reference systems. CO₂ equivalent emission factor: Used in the ecological assessment of the reference systems, this factor is expressed in kg CO₂-eq per kWh. Note: Additional variable or consumption-dependent costs (e.g., portions of network costs) cannot be defined separately later in the tool. Such costs should be integrated directly into the fuel costs.
Further economic boundary conditions include the available capital for investments (equity) and the loan interest rate. When an investment is required, the tool assumes that all available equity is used for the initial investment. If a reinvestment becomes necessary during the 20-year period (i.e., when the installation lifetime is shorter than 20 years), the subsequent investment is assumed to be financed entirely without equity.
The currency displayed in the tables and graphs can be easily changed by selecting one of the predefined options (EUR, USD, PLN, or HRK). This feature is intended to facilitate the use of the tool in regions outside the Eurozone. Please note that the numerical values within the Excel workbook are dimensionless—changing the displayed currency does not automatically convert them. Therefore, all values must be manually adjusted after changing the “currency used” setting.
RES Alternatives
This sheet defines the reference case as well as a set of alternative heat supply portfolios. The first two values, heat demand and heat production capacity, represent the main technical boundary conditions. In addition, user must specify an installation lifetime, which refers to the number of years after which the heating system requires a reinvestment equivalent to the initial investment. The technology mix determines how the required heat is produced. Here, the share of total heat demand covered by each technology can be defined. Next, the technology efficiency factors must be entered. These values represent the energy conversion efficiencies and are used to calculate the amount of driving energy required. The resulting fuel consumption is shown in the fuel mix section, both in MWh/a and as a percentage. These intermediate results form the basis for the fuel cost and emissions calculations. The final input section focuses on economic parameters. For each case, users must define the required investment, the share of the investment that is subsidised (if applicable), and the loan period. Note that equity and the loan interest rate are identical for all cases and are defined in the Boundary Conditions sheet. Lastly, the fixed annual costs must be entered, divided into capacity-dependent costs and fully fixed costs.
Next, the results are presented. The results include the following values, - Yearly costs: The average annual costs over a 20-years period. These are divided into variable and fixed costs. - Variable costs: These consist primarly of fuel costs (and, where applicable, grid-related costs if they have been integrated into the fuel price). - Fixed costs: Fixed costs include both the investment costs and the fixed operating and maintenance costs of the system. In most cases, the investment cost component represents the largest share of fixed costs. Therefore, an additional row—"thereof investment costs"—indicates the average annualised investment cost. Using the calculated annual heat costs and the corresponding heat supplied, the tool determines the effective heat costs. The results table also shows the effective heat cost ratio, expressed as the percentage deviation from the district heating (DH) reference system, which is set at 100%. In addition, the tool calculates the annual CO₂-equivalent emissions, expressed in tonnes per year. Selected results from the table are also visualised in two different diagrams.
Additional explanatory notes
Average investment costs
To ensure a fair comparison, the states of all heat production systems are assumed to be equivalent at the beginning and end of the considered period (20 years, as noted above). In this context, all technical solutions use the same amount of available capital to finance the investment, except in cases where the required investment is less than the available equity—in such cases, no loan is needed. At the end of year 20, the tool accounts for remaining payments and the residual value of the installation as follows: Remaining annual payments: All outstanding payments are made; no discounting is applied, i.e., interest is also paid. Residual value: The installation is “sold” at its residual value, calculated by assuming linear depreciation over its lifetime. For example, a component that has reached half of its lifetime is assumed to retain 50% of its initial investment value (excluding any subsidy).

## Boundary conditions
Fill in yellow colored cells, i.e. input cells -->
|  | Do not overwrite white cells formulas --> |  |  |  | Currency | EUR | Economic boundary conditions | Value | Unit
[8 empty] | Available capital (= max Equity) | 0 | [EUR]
| Fuel data | [6 empty] | Loan interest rate | 4% | [%]
| Fuel type | Parameters | Value | Unit | Notes
| Biomass (pellets) | Net heating value | 4.8 | [kWh/kg] | The Austrian energy agency (reference 3) provides net (lower) heating value of 5.27 for dry mass and 4.8 kWh for fresh mass of compressed wood (wood pellets). (*According to ÖNORM M 7135, the moisture content of compressed wood must be ≤10%). Additionally, reference 1) analyzed 21 wood pellet samples from different countries. The observed minimum, maximum and average net heating values were 5.17, 5.39 and 5.28 kWh/kg, respectively. Reference 2) provides price indices for pellets in Austria. According to this source, the pellet price in Austria at 1.11.2025 is 356 €/t (based on a purchase of 6 tonnes). Historical prices ranged from a maximum of 634 €/t in October 2022 to a minimum of 232 €/t in April 2019. Other sources, such as reference 8), report higher prices. For example, 1050 kg pellets (5.3 - 4.9 kWh/kg) cost around 629 EUR (gross price, including transport), corresponding to approximately 0.599 EUR/kg or 122-113 EUR/kWh (gross). The CO₂-equivalent emission factor is assumed to be 39 g/kWh as given in reference 13) for wood pellets (wood-mixture) at 50 kW capacity.
|  | Fuel price (base year) | 0.356 | [EUR/kg]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year - NCV) | 74.1667 | [EUR/MWh]
|  | Average heat price 20-years | 110.427 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 39 | [kg CO₂ eq. /MWh]
| Waste heat | Net heating value |  | [kWh/m³] | The temperature of the waste heat is not predefined. Both the temperature drop and the volume flow rate are case-specific, which makes it difficult to determine kWh/m3 and the associated price in advance. Therefore, the heat price for the base year must be entered directly. The CO₂-equivalent emission factor is assumed to be 22 g/kWh, as specified in reference 15).
|  | Fuel price (base year) |  | [EUR/m³]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year) | 10 | [EUR/MWh]
|  | Average heat price 20-years | 14.889 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 22 | [kg CO₂ eq. /MWh]
| Biomass (wood chips) | Net heating value | 893 | [kWh/m³ (loose)] | The net heating value for a specific wood mix can be calculated using the Excel tool referenced in 3). An exemple value of 893 kWh/m³ corresponds to a mixture "pine" and "wood chips" with 30 % moisture content. The net (lower) heating value per kilogram of dry mass is 5.27 kWh/kg, and per kilogram of fresh mass is 3.49 kWh/kg (i.e. 256 kg/m3) The CO₂-equivalent emission factor is assumed to be 10 g/kWh as given in reference 13) for wood chips derived mixed forest wood.
|  | Fuel price (base year) | 33 | [EUR/m³ (loose)]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year - NCV) | 36.9541 | [EUR/MWh]
|  | Average heat price 20-years | 55.0211 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 10 | [kg CO₂ eq. /MWh]
| Natural gas | Net heating value | 11.3 | [kWh/m³] | Natural gas is a mixture of gases, with methane as the predominant component. Its net heating value in the "Marktgebiet Ost" region is 11.33 kWh/m3, according to reference 11). Information on the current natural gas prices in Austria can be found on the E-Control website (reference 9). The CO₂ equivalent emission factor is assumed to be 247 g/kWh, as given in reference 14). Further details on this value are procided in reference 13).
|  | Fuel price (base year) | 1.5 | [EUR/m³]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year - NCV) | 132.7434 | [EUR/MWh]
|  | Average heat price 20-years | 197.6421 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 247 | [kg CO₂ eq. /MWh]
| Oil | Net heating value | 10 | [kWh/l] | Current and historical data on oil prices in Austria can be found in reference 12). Since 2022, oil prices have no fallen below 1 EUR/l. The CO₂ equivalent emission factor is assumed to be 310 g/kWh as given in reference 14). Further details on this value are provided in reference 13).
| (heating oil) | Fuel price (base year) | 1 | [EUR/l]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year) | 100 | [EUR/MWh]
|  | Average heat price 20-years | 148.8904 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 310 | [kg CO₂ eq. /MWh]
| Coal | Net heating value | 8 | [kWh/kg] | An exemple net heating value of 8.06 kWh/kg for bituminous coal is reported in reference 6). According to reference 8), the gross price of bituminous coal ("Steinkohle"), including transport, is approximately 0.94 EUR/kg. The fuel supplier guarantees a minimm net heating value up to 8 kWh/kg. Lignite ("Braunkohle") is slightly cheaper but has a lower net heating value. Prices and net heating values for lignite coal are also provided in reference 8). The CO₂ equivalent emission factor is assumed to be 375 g/kWh, as given in reference 14). Further details on this value are provided in reference 13).
|  | Fuel price (base year) | 0.55 | [EUR/kg]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year) | 68.75 | [EUR/MWh]
|  | Average heat price 20-years | 102.3621 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 375 | [kg CO₂ eq. /MWh]
| Electricity | Net heating value | 1 | [kWh/kWhel] | Electricity prices in Austria can be consulted in E-Control website (reference 10). At the European level, sources such as 16) (e.g. the Data Dashborad on Energy Prices and the Report on energy prices and costs in Europe) provide detailed information. Reference 17) also offers a good overview on electricity prices. The CO₂ equivalent emission factor is assumed to be 74 g/kWh, as given in reference 15) for the period 2026-2035.
| (supply mix) | Fuel price (base year) | 268 | [EUR/MWhel]
|  | Averaged price development | 4% | [%/a]
|  | Heat price (base year) | 268 | [EUR/MWh]
|  | Average heat price 20-years | 399.0263 | [EUR/MWh]
|  | CO₂ equivalent emission factor | 74 | [kg CO₂ eq. /MWh]
n° | Reference list
1) | Obernberger, I. Thek, G. Physical characterisation and chemical composition of densified biomass fuels with regard to their combustion behaviour. Biomass and Bioenergy 27 (2004)
2) | proPellets Austria. https://www.propellets.at/aktuelle-pelletpreise
3) | Solid Biomass fuel parameters calculation tool v1.8. Austrian energy agency
4) | Land- und Forstwirtschaftliche Erzeugerpreise. Statistik Austria
5) | Landwirtschaftskammer Niederösterreich: Energieholzindex
6) | Fuels - Higher and Lower calorific values. The engineering ToolBox. https://www.engineeringtoolbox.com/fuels-higher-calorific-values-d_169.html
7) | Energiepreise im Vergleich. Energieinstitut Vorarlberg. https://www.energieinstitut.at/buerger/haustechnik-energieversorgung/energiepreise-im-vergleich/
8) | https://www.brennstoffe.kaufen/
9) | https://www.e-control.at/gewerbe-gaspreis-monitor
10) | https://www.e-control.at/gewerbe-strompreis-monitor
11) | Gas-Systemnutzungsentgelte-Verordnung 2013, GSNE-VO 2013, Fassung vom 15.06.2020
12) | https://www.heizoel24.at/charts/heizoel
13) | Erläuternde Bemerkungen OIB-RL 6. Energieeinsparung und Wärmeschutz. OIB-220.6-027/19. April 2019
14) | OIB-Richtlinie 6. Energieeinsparung und Wärmeschutz. OIB-330.6-026/19. April 2019
15) | Erläuternde Bemerkungen OIB-RL 6. Energieeinsparung und Wärmeschutz. OIB-330.6-140/25. September 2025
16) | European comission. Energy prices and costs in Europe. https://energy.ec.europa.eu/data-and-analysis/energy-prices-and-costs-europe_en
17) | EMBER. https://ember-energy.org/data/european-wholesale-electricity-price-data/

## RES Alternatives
Fill in yellow-colored cells, which are designated for user input. Other cells should not be edited -->
Do not overwrite white cells formulas -->
Description | Unit | Heating system | [9 empty] | Notes
Technical parameters |  | DH system (reference) | Waste heat + Heat pump | Biomass boiler + Solar thermal | Biomass boiler (wood chips) | Ambient/Geothermal + heat pump | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | The heat production capacity in MW is primarly used to calculate capacity-dependent fixed costs (see row 67). Optionally, it can also be used to define size-dependent investment costs. The installation lifetime (years): The lifetime should be at least 10 years. If a value below 10 is entered, the cell will be highlighted in red, and the value will be automatically corrected to 10 years in the background.
Heat demand (heat produced) | [MWh/a] | 27600 | 27600 | 27600 | 27600 | 27600 | 27600 | 27600 | 27600 | 27600 | 27600
Heat production capacity | [MW] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Installation lifetime | [a] | 20 | 20 | 30 | 35 | 40 | 40 | 40 | 40 | 40 | 40
Technology mix
Pellets boiler | [%] | [10 empty] | This section is used to define the origin of the heat. For the heat pump case, two scenarios are considered: 1. Using waste heat as the source 2. Using ambient heat (air and/or geothermal) as the source The actual amounts of electricity and waste heat consumed will be calculated later, once the COP (Coefficient of Performance) of the heat pump is specified.
Wood chips boiler | [%] | 30% | 50% | 80% | 100% |  | 50% | 75% | 75% | 75%
Heat pump (source: waste heat) | [%] |  | 50% | [5 empty] | 25%
Heat pump (source: ambient/geothermal) | [%] |  |  |  |  | 100% |  |  |  | 25% | 80%
Waste heat (direct use) | [%]
Solar thermal | [%] |  |  | 20%
P2H | [%]
Gas boiler | [%] | 70% |  |  |  |  | 50% | 25% |  |  | 10%
Oil boiler | [%] | [9 empty] | 10%
Coal boiler | [%]
| *Check | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Technology efficiency factors (yearly averaged values)
Pellets boiler | [-] | [10 empty] | This section accounts for the efficiency of the energy conversion process, i.e., it calculates the amount of primary energy (electricity, gas, biomass, etc.) required to produce the useful heat supplied to the district heating network.
Wood chips boiler | [-] | 85% | 85% | 85% | 85% |  | 85% | 85% | 85% | 85%
Heat pump COP (source: waste heat) | [-] |  | 3.5 | [5 empty] | 3.5
Heat pump COP (source: ambient/geothermal) | [-] |  |  |  |  | 3 |  |  |  | 3 | 3
Waste heat (direct use) | [-]
Solar thermal electricity consumption | [kWhel/kWhth] |  |  | 3%
P2H | [-]
Gas boiler | [-] | 82% |  |  |  |  | 85% | 85% |  |  | 85%
Oil boiler | [-] | [9 empty] | 85%
Coal boiler | [-]
Fuel mix (intermediate results)
Pellets | [MWh/a] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | This section displays intermediate results, specifically the fuel mix in MWh/a. These values are calculated based on the parameters defined above, primarily the heat demand, technology mix, and efficiency factors.
Wood chips | [MWh/a] | 9741.1765 | 16235.2941 | 25976.4706 | 32470.5882 | 0 | 16235.2941 | 24352.9412 | 24352.9412 | 24352.9412 | 0
Waste heat | [MWh/a] | 0 | 9857.1429 | 0 | 0 | 0 | 0 | 0 | 4928.5714 | 0 | 0
Electricity | [MWh/a] | 0 | 3942.8571 | 165.6 | 0 | 9200 | 0 | 0 | 1971.4286 | 2300 | 7360
Gas | [MWh/a] | 23560.9756 | 0 | 0 | 0 | 0 | 16235.2941 | 8117.6471 | 0 | 0 | 3247.0588
Oil | [MWh/a] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.0588
Coal | [MWh/a] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy input | [MWh/a] | 33302.1521 | 30035.2941 | 26142.0706 | 32470.5882 | 9200 | 32470.5882 | 32470.5882 | 31252.9412 | 26652.9412 | 13854.1176
Annual efficiency (Heat delivered/Energy input) | [%] | 82.88% | 91.89% | 105.6% | 85% | 300% | 85% | 85% | 88.31% | 103.6% | 199.2%
Fuel mix (intermediate results)
Waste heat | [%] |  | 32.82% | [5 empty] | 15.77% |  |  | This section shows intermediate results, specifically the fuel mix expressed as a percentage of the total energy supplied.
Electricity | [%] |  | 13.13% | 0.6335% | 0% | 100% | 0% | 0% | 6.308% | 8.629% | 53.12%
Biomass | [%] | 29.25% | 54.05% | 99.37% | 100% |  | 50% | 75% | 77.92% | 91.37%
Thereof …
Pellets | [%]
Wood chips | [%] | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100%
Fossil fuel | [%] | 70.75% |  |  |  |  | 50% | 25% |  |  | 46.87%
Thereof …
Gas | [%] | 100% |  |  |  |  | 100% | 100% |  |  | 50%
Oil | [%] | [9 empty] | 50%
Coal | [%]
| *Check | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Investment
Investment (without subsidy) | [EUR] | 6000000 | 18000000 | 15000000 | 15000000 | 12000000 | 10000000 | 10000000 | 10000000 | 10000000 | 10000000 | Investment Costs (without subsidy): It is recommended to adapt investment costs to local prices. These costs should be redefined whenever system capacities change (e.g., moving from small to large systems), unless investment costs are defined as a function of installed capacity. Estimating costs at early planning stages can be challenging. In addition to own experience, technical catalogues (e.g., references 1 and 2) or technology-specific publications (e.g., references 3, 4, and 5) can be helpful. Investment costs should include the heat production units and any additional necessary equipment (e.g., fuel silos). To ensure a fair comparison, the system boundaries must be clearly defined and applied equally across all systems. Loan Period: The loan period is calculated based on the investment to keep the consumer effort (annuity) comparable across different heating systems. The loan period is limited by the installation lifetime. Equivalent CO₂ Emission Factor: This is calculated based on the fuel mix of the system.
Subsidy on investment | [%] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Equity | [EUR] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Invest to be financed | [EUR] | 6000000 | 18000000 | 15000000 | 15000000 | 12000000 | 10000000 | 10000000 | 10000000 | 10000000 | 10000000
Loan period | [a] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Averaged investment annuity payments (-residual value) | [EUR] | 404734.9517 | 1214204.855 | 761837.3792 | 690408.8077 | 509469.9033 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528
Economic parameters
Fixed costs | [EUR/a] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed costs (capacity dependent) | [EUR/(MW.a)] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable costs (e.g. O&M - additional to fuel costs, related to energy input) | [EUR/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Averaged variable costs (fuel costs) | [EUR/MWh] | 155.9242 | 87.0093 | 57.2002 | 55.0211 | 399.0263 | 126.3316 | 90.6763 | 70.3921 | 84.7068 | 293.2013
Total variable costs | [EUR/MWh] | 155.9242 | 87.0093 | 57.2002 | 55.0211 | 399.0263 | 126.3316 | 90.6763 | 70.3921 | 84.7068 | 293.2013
CO₂ equivalent emission factor (technology mix) | [kg CO₂ eq. /MWh] | 177.6754 | 22.3398 | 10.4054 | 10 | 74 | 128.5 | 69.25 | 15.9295 | 15.5228 | 169.8594
Emissions of CO₂ equivalent | [t/a] | 5916.9727 | 670.9815 | 272.0191 | 324.7059 | 680.8 | 4172.4706 | 2248.5882 | 497.8437 | 413.7294 | 2353.2518
Savings of CO₂ equivalent respect to reference | [t/a] |  | 5245.9912 | 5644.9536 | 5592.2669 | 5236.1727 | 1744.5022 | 3668.3845 | 5419.129 | 5503.2433 | 3563.721
Taxable (fossil fuel) emissions of CO₂ equivalent | [t/a] | 5819.561 | 216.8571 | 0 | 0 | 0 | 4010.1176 | 2005.0588 | 108.4286 | 0 | 1808.6118
CO2 tax | 0 | [EUR/t] | Carbon tax: Applied to emissions of CO2 equivalent of fossil fuel heat production and waste heat.
Results
Description | Unit | DH system (reference) | Waste heat + Heat pump | Biomass boiler + Solar thermal | Biomass boiler (wood chips) | Ambient/Geothermal + heat pump | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Results notes
Yearly costs | [EUR/a] | 5597346.0962 | 3827555.265 | 2257169.7446 | 2476975.8301 | 4180511.4302 | 4526619.622 | 3368872.4486 | 2624516.969 | 2682243.9013 | 4486602.9098
Variable costs | [EUR/a] | 5192611.1445 | 2613350.41 | 1495332.3654 | 1786567.0224 | 3671041.5268 | 4102061.3692 | 2944314.1958 | 2199958.7162 | 2257685.6485 | 4062044.657
Of which CO2 equivalent emissions costs | [EUR/a] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed costs | [EUR/a] | 404734.9517 | 1214204.855 | 761837.3792 | 690408.8077 | 509469.9033 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528
Of which investment costs | [EUR/a] | 404734.9517 | 1214204.855 | 761837.3792 | 690408.8077 | 509469.9033 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528
Share fixed costs | [%] | 7.231% | 31.72% | 33.75% | 27.87% | 12.19% | 9.379% | 12.6% | 16.18% | 15.83% | 9.463%
Share variable costs | [%] | 92.77% | 68.28% | 66.25% | 72.13% | 87.81% | 90.62% | 87.4% | 83.82% | 84.17% | 90.54%
Effective heat production costs | [EUR/MWh] | 202.8024 | 138.6795 | 81.7815 | 89.7455 | 151.4678 | 164.008 | 122.0606 | 95.0912 | 97.1828 | 162.5581
Share fixed costs | [EUR/MWh] | 14.6643 | 43.9929 | 27.6028 | 25.0148 | 18.4591 | 15.3825 | 15.3825 | 15.3825 | 15.3825 | 15.3825
Share variable costs | [EUR/MWh] | 188.1381 | 94.6866 | 54.1787 | 64.7307 | 133.0088 | 148.6254 | 106.6781 | 79.7086 | 81.8002 | 147.1755
n° | Reference list
1) | KEA Klimaschutz- und Energieagentur Baden-Württemberg GmbH. https://www.kea-bw.de/waermewende/angebote/downloads.
2) | Danish Energy Agency. https://ens.dk/en/analyses-and-statistics/technology-catalogues
3) | Rieberer, R., et al. Industrial Heat Pumps, Second Phase. IEA Heat Pump Technology (HPT) Programme Annex 48. Task 4: Training materials for industrial heat pumps. August 2019.
4) | Benjamin, Z. et al. High-Temperature Heat Pumps. Task 1 – Technologies. IEA Heat Pump Technology (HPT) Programme Annex 58. Report no. HPT-AN58-2. August 2023.
5) | Solar Heat and Energy Economics in Urban Environments. IEA SHC Task 52. Subtask B and C. https://task52.iea-shc.org/.

## HelpSheet (hidden)
This sheet contains supporting calculations for the tool and is not intended to be changed by the user.
|  |  | 5 | 6 | 7 | 8 |  | 10 | 11 | 12 | 13 | 14
5 | Fuel types |  | EUR | CHF | PLN | CZK | 5 | EUR | CHF | PLN | CZK
6 | Natural gas | [m³/a] | [EUR/m³] | [CHF/m³] | [PLN/m³] | [CZK/m³] | 6 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Basic charge
7 | Oil | [l/a] | [EUR/l] | [CHF/l] | [PLN/l] | [CZK/l] | 7 | [EUR/(MW.a)] | [CHF/(MW.a)] | [PLN/(MW.a)] | [CZK/(MW.a)] | Meter charge
8 | Biomass (pellets) | [kg/a] | [EUR/kg] | [CHF/kg] | [PLN/kg] | [CZK/kg] | 8 | [EUR/MWh] | [CHF/MWh] | [PLN/MWh] | [CZK/MWh] | Energy charge
9 | Electricity | [kWhel/a] | [EUR/MWhel] | [CHF/MWhel] | [PLN/MWhel] | [CZK/MWhel] | 9 | [EUR] | [CHF] | [PLN] | [CZK] | Investment (without subsidy)
10 | Coal | [kg/a] | [EUR/kg] | [CHF/kg] | [PLN/kg] | [CZK/kg] | 10 | [EUR] | [CHF] | [PLN] | [CZK] | Invest to be financed
11 | Biomass (wood chips) | [m³ (loose)/a] | [EUR/m³ (loose)] | [CHF/m³ (loose)] | [PLN/m³ (loose)] | [CZK/m³ (loose)] | 11 | [EUR] | [CHF] | [PLN] | [CZK] | Equity
12 | Waste heat | [m³/a] | [EUR/m³] | [CHF/m³] | [PLN/m³] | [CZK/m³] | 12 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Maintenance costs
13 | Condensing boiler | [%/a] | [EUR/MWh] | [CHF/MWh] | [PLN/MWh] | [CZK/MWh] | 13
14 |  | [a] | Fuel price [EUR/MWh] | Fuel price [CHF/MWh] | Fuel price [PLN/MWh] | Fuel price [CZK/MWh] | 14
15 |  |  | [EUR] | [CHF] | [PLN] | [CZK] | 15 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Effective heating cost
16 |  |  | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | 16 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Averaged investment costs
17 |  |  | [EUR/t] | [CHF/t] | [PLN/t] | [CZK/t] | 17 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | There of.. Financing costs
16 | [6 empty] | 18 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Fixed costs
19 | [6 empty] | 19 | [EUR/a] | [CHF/a] | [PLN/a] | [CZK/a] | Variable costs
20 | [6 empty] | 20 | [EUR/MWh] | [CHF/MWh] | [PLN/MWh] | [CZK/MWh] | Effective heat cost
|  |  | Currency start at column | 5
|  |  | Currency selected | EUR
|  |  | Column | 5
Fuel price [EUR/MWh]
|  |  | Currency start at column | 10
|  |  | Column HeatSupplyT | 10
Fuel prices in .. [EUR/MWh]
Year n° | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Fuel type \ year | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | Avg - 10 years | Avg - 20 years
Biomass (pellets) | 74.1667 | 77.1333 | 80.2187 | 83.4274 | 86.7645 | 90.2351 | 93.8445 | 97.5983 | 101.5022 | 105.5623 | 109.7848 | 114.1762 | 118.7432 | 123.493 | 128.4327 | 133.57 | 138.9128 | 144.4693 | 150.2481 | 156.258 | 89.0453 | 110.427
Biomass (wood log) | 10 | 10.4 | 10.816 | 11.2486 | 11.6986 | 12.1665 | 12.6532 | 13.1593 | 13.6857 | 14.2331 | 14.8024 | 15.3945 | 16.0103 | 16.6507 | 17.3168 | 18.0094 | 18.7298 | 19.479 | 20.2582 | 21.0685 | 12.0061 | 14.889
Biomass (wood chips) | 36.9541 | 38.4323 | 39.9695 | 41.5683 | 43.2311 | 44.9603 | 46.7587 | 48.6291 | 50.5742 | 52.5972 | 54.7011 | 56.8891 | 59.1647 | 61.5313 | 63.9925 | 66.5522 | 69.2143 | 71.9829 | 74.8622 | 77.8567 | 44.3675 | 55.0211
N. gas | 132.7434 | 138.0531 | 143.5752 | 149.3182 | 155.291 | 161.5026 | 167.9627 | 174.6812 | 181.6685 | 188.9352 | 196.4926 | 204.3523 | 212.5264 | 221.0275 | 229.8686 | 239.0633 | 248.6258 | 258.5709 | 268.9137 | 279.6702 | 159.3731 | 197.6421
Oil | 100 | 104 | 108.16 | 112.4864 | 116.9859 | 121.6653 | 126.5319 | 131.5932 | 136.8569 | 142.3312 | 148.0244 | 153.9454 | 160.1032 | 166.5074 | 173.1676 | 180.0944 | 187.2981 | 194.79 | 202.5817 | 210.6849 | 120.0611 | 148.8904
Coal | 68.75 | 71.5 | 74.36 | 77.3344 | 80.4278 | 83.6449 | 86.9907 | 90.4703 | 94.0891 | 97.8527 | 101.7668 | 105.8375 | 110.071 | 114.4738 | 119.0528 | 123.8149 | 128.7675 | 133.9182 | 139.2749 | 144.8459 | 82.542 | 102.3621
Electricity | 268 | 278.72 | 289.8688 | 301.4636 | 313.5221 | 326.063 | 339.1055 | 352.6697 | 366.7765 | 381.4476 | 396.7055 | 412.5737 | 429.0766 | 446.2397 | 464.0893 | 482.6529 | 501.959 | 522.0373 | 542.9188 | 564.6356 | 321.7637 | 399.0263
Currencies
Name | Symbol | CODE (ISO 4217)
Euro | € | EUR
Swiss franc | Fr. | CHF
Polish Złoty | zł | PLN
Czech Koruna | Kč | CZK
| Interest rate | Predefined heating systems
| 4% | DH system (reference) | Waste heat + Heat pump | Biomass boiler + Solar thermal | Biomass boiler (wood chips) | Ambient/Geothermal + heat pump | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Subsidy | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Equity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Amount to be financed | 6000000 | 18000000 | 15000000 | 15000000 | 12000000 | 10000000 | 10000000 | 10000000 | 10000000 | 10000000
| Loan period [a] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Lifetime [a] | 20 | 20 | 30 | 35 | 40 | 40 | 40 | 40 | 40 | 40
| Installation whole "lifes" used in 20 years | 1 | 1 | 0.66667 | 0.57143 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Life remaining installation (lim+ t->20) | 1 | 1 | 0.33333 | 0.42857 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Annuity (with subsidy) | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| Annuity due to reinvestment (without subsidy) | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| Total amount to be payed (reinvest) | 8094699.0334 | 24284097.1002 | 20236747.5835 | 20236747.5835 | 16189398.0668 | 13491165.0556 | 13491165.0556 | 13491165.0556 | 13491165.0556 | 13491165.0556
Value use to calculate the rest value | Remaining lifetime installation [a] | 20 | 20 | 10 | 15 | 20 | 20 | 20 | 20 | 20 | 20
| Rest value installation (linear value deprecation) | 6000000 | 18000000 | 5000000 | 6428571.4286 | 6000000 | 5000000 | 5000000 | 5000000 | 5000000 | 5000000
This value is applied to year = 20 | "Bonus" at 20 years (Rest value - open payments) | 0 | 0 | 5000000 | 6428571.4286 | 6000000 | 5000000 | 5000000 | 5000000 | 5000000 | 5000000
As the rest value is considered so are they payments that need to be done after year 20 to fully pay the installation | Open payments | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Year n° | Annuity + equity
| 1 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 2 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 3 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 4 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 5 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 6 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 7 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 8 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 9 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 10 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 11 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 12 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 13 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 14 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 15 | 539646.6022 | 1618939.8067 | 1349116.5056 | 1349116.5056 | 1079293.2045 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037 | 899411.0037
| 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20 | 0 | 0 | -5000000 | -6428571.4286 | -6000000 | -5000000 | -5000000 | -5000000 | -5000000 | -5000000
[EUR] | Sum of payments | 8094699.0334 | 24284097.1002 | 15236747.5835 | 13808176.1549 | 10189398.0668 | 8491165.0556 | 8491165.0556 | 8491165.0556 | 8491165.0556 | 8491165.0556
[EUR/a] | Averaged investment | 404734.9517 | 1214204.855 | 761837.3792 | 690408.8077 | 509469.9033 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528 | 424558.2528
Accumulated payments
| Year | DH system (reference) | Waste heat + Heat pump | Biomass boiler + Solar thermal | Biomass boiler (wood chips) | Ambient/Geothermal + heat pump | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5
| 1 | 5597346.0962 | 3827555.265 | 2257169.7446 | 2476975.8301 | 4180511.4302 | 4526619.622 | 3368872.4486 | 2624516.969 | 2682243.9013 | 4486602.9098
| 2 | 11194692.1924 | 7655110.5299 | 4514339.4891 | 4953951.6603 | 8361022.8603 | 9053239.2439 | 6737744.8971 | 5249033.9379 | 5364487.8026 | 8973205.8196
| 3 | 16387303.3369 | 10268460.9399 | 6009671.8545 | 6740518.6827 | 12032064.3872 | 13155300.6131 | 9682059.0929 | 7448992.6541 | 7622173.4511 | 13035250.4766
| 4 | 16792038.2886 | 11482665.7949 | 6771509.2337 | 7430927.4904 | 12541534.2905 | 13579858.8659 | 10106617.3457 | 7873550.9069 | 8046731.7038 | 13459808.7293
| 5 | 17196773.2403 | 12696870.6499 | 7533346.6129 | 8121336.2981 | 13051004.1938 | 14004417.1187 | 10531175.5985 | 8298109.1596 | 8471289.9566 | 13884366.9821
| 6 | 17196773.3126 | 12696870.9671 | 7533346.9504 | 8121336.5769 | 13051004.3157 | 14004417.2125 | 10531175.7245 | 8298109.3214 | 8471290.1149 | 13884367.0768
| 7 | 17196774.2403 | 12696871.6499 | 7533347.6129 | 8121337.2981 | 13051005.1938 | 14004418.1187 | 10531176.5985 | 8298110.1596 | 8471290.9566 | 13884367.9821
| 8 | 17196977.0427 | 12697010.3294 | 7533429.3944 | 8121427.0436 | 13051156.6616 | 14004582.1266 | 10531298.6591 | 8298205.2508 | 8471388.1394 | 13884530.5402
| 9 | 17196991.707 | 12697054.3224 | 7533456.9972 | 8121452.0585 | 13051175.1207 | 14004597.5092 | 10531314.0416 | 8298220.6334 | 8471403.5219 | 13884545.9227
| 10 | 17197179.8451 | 12697149.009 | 7533511.1759 | 8121516.7891 | 13051308.1295 | 14004746.1346 | 10531420.7197 | 8298300.342 | 8471485.3221 | 13884693.0983
| 11 | 17197179.8451 | 12697149.009 | 7533511.1759 | 8121516.7891 | 13051308.1295 | 14004746.1346 | 10531420.7197 | 8298300.342 | 8471485.3221 | 13884693.0983
| 12 | 17203096.8178 | 12697819.9905 | 7533783.195 | 8121841.495 | 13051988.9295 | 14008918.6052 | 10533669.3079 | 8298798.1857 | 8471899.0515 | 13887046.35
| 13 | 17203096.8178 | 12703065.9817 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14010663.1073 | 10537337.6924 | 8304217.3148 | 8477402.2949 | 13890610.071
| 14 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 15 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 16 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 17 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 18 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 19 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
| 20 | 17208916.3788 | 12703282.8389 | 7539428.1486 | 8127433.7619 | 13057225.1022 | 14014673.225 | 10539342.7512 | 8304325.7433 | 8477402.2949 | 13892418.6828
|  | 325218637.434 | 236436634.3108 | 140135848.6256 | 151593608.1071 | 245982884.4598 | 264469236.9871 | 198460682.1049 | 156016745.3808 | 159306387.6029 | 262171019.8363